Whereville

The Village of Whereville, population 245, is located in the central midwest.  The community water system was constructed in 1950 and is comprised of a well, water tower, chemical addition for fluoride, disinfection and sequestering of iron. The distribution system has 2-inch, 4-inch and some 6-inch cast iron water mains.  The water system serves only the Village of Whereville.

The water facilities are in compliance with all regulations at this time.

Climate and Precipitation

The Village's climate has cold winters and hot summers with considerable humidity. The average high and low temperature for the warmest and coldest months are 85.2°F and 64.8°F (July) with 32.0°F and 16.7°F (January).  Precipitation is an important factor to agriculturally oriented areas such as Whereville, as is precipitation distribution throughout the year. Again, according to the data, the Whereville planning area has an annual average precipitation of 41.0 inches. Of this, approximately 24.9 inches falls during the growing season (April 1 to October I). The area average snowfall is 26.2 inches.

Topography

The topography of Whereville planning area is characterized by the gently sloping terrain. The elevation ranges from a high point of approximately 696 feet (MSL) to a low point of approximately 685 feet (MSL). The high point is in the southwest comer of the community with the railroad running along a ridge line which bisects the community from the southwest to the northeasterly portion of the community. Drainage falls generally westerly and easterly from the railroad. There is no drainage way within the community.

Economy and Demographics

The Whereville planning area is predominantly a residential ( 90%) and agricultural area. Currently, there are no planned or proposed major industrial/commercial growth that would impact the local Whereville economy. There are no stores or service stations within the system.

The Village economic and demographic profile reports that the median age of the population was 40.8 years with 50% of the population over the age of 65. The total number of households reported in the year 2024 was 102. The median household income increased from $25,625 in 1990 to $39,659 in the year 2024.

Population

The Census data shows that the County population declined from 1980 to 1990 with a partial reversal from 1990 to 2000. The increase was 1.8 % during the most recent l0-year census period. This trend is paralleled by the communities in the County. The Village of Whereville exhibited the same trend. The 2024 population for the community was 245. A conservative increase in population of 5.0% per 10-year increment is assumed

Land Use

The Village has a small commercial area is located in the west central portion of the community. This includes a fire station and a post office along with the offices for the water system.  Whereville Elementary School, is located on the north central boundary of the community. A current service industry, truck maintenance facility is located on the southeast boundary of the village.

Water Treatment and Distribution Discharges

The Village owns and operates the public water supply. The system was constructed in 1950. The water is provided by one well. There is a second well adjacent to the current well that is not in service at this time.  The water is treated with chemical addition for disinfection, fluoride addition and iron sequestering and discharged to distribution. The treatment system does not generate any waste water which is discharged to local drainage ways. The system pressure and storage is provided by a single water tower. The distribution system is principally 2 inch and 4 inch cast iron water mains. All facilities were built in 1950 with only minor water main replacements or extensions and a new replacement well. The system does not have any current EPA rules and regulations compliance issues to be resolved. The system does exhibit poor water pressure and limited ability to deliver suitable volume under the low pressure conditions at the homes.

Water quality is partially assisted by frequent flushing of the water mains. Distribution system maintenance requires periodic water main flushing to minimize water quality issues in dead ends on the system. The quantity of the discharges are small, less than 1000 gallons per hydrant. The number of hydrants where flushing occurs is less than 10 and the usual cycle for flushing is quarterly.

Wastewater Treatment Systems

The Village does not have sewer collection or treatment systems. All wastewater generated in the community is domestic in nature and treated by septic tank. The surface soils are poorly drained and thus require large septic tank leach fields. The community does not exhibit water quality issues in the drainage ditches from connections of septic tanks to field tile outlets.

Future Land Use

Currently, a zoning map is not available for the Village of Whereville. Recent history shows that significant residential or commercial development has not occurred. Minor growth is anticipated due to the population growth projections. Future residential developments are anticipated to be located along the east side and south side of the community. The anticipated population growth suggests that approximately 15 acres (20 lots) of new residential development would be required over the next 20 years.

Current Water Usage and Projected Water Usage

Water usage throughout the Village of Whereville serves as the basis for projection of future flows. The Village of Whereville currently has 110 water services on record. The annual water use for the year 2023 was recorded as 7,761,000 gallons. The total water use for the first eight months of 2024 was 4,963,000 gallons. The average day use for the 2 years reviewed was 21,140 gal/day and 20,508 gal/day respectively.

The population estimate for the community for the year 2025 and 2026 is based on the population projections per previous sections would indicate population for 2025 and 2026 should be 248 persons and 252 persons respectively. The per capita consumptive rate for 2025 and 2026 would be 79.5 gal/day and 76.8 gal/day respectively.

The Administrative Code Rules and Regulations establishes rates of use for design purposes.

Average Day Rate of Use= 2 x Average Day Use converted to gpm in 24 hours. Average Day Rate of Use= 2 x 25,000 gpd / 1440 minutes/day= 35 gpm

Maximum Daily Rate of Use= 1.5 x Average Day Rate of Use. Maximum Daily Rate of Use= 1.5 x 35 gpm = 52 gpm

Maximum Hour Rate of Use= 2 x Maximum Daily Rate of Use Maximum Hour Rate of Use= 2 x 52 gpm = 104 gpm.

Fire Service Requirements

Basis for Analysis

It is recommended fire hydrants should be operated and maintained in accordance with American Water Works Association Manual of Water Supply Practices No. M17.

Fire Flow Analysis Results

The Village is currently rated Class 8 by the Insurance Services Office (I.S.O.) according to the Fire Department for the community. The ratings are on a scale of 1 to 10 with Class 1 as the highest. Although the amount of water used in a typical year for extinguishing fires is usually a negligible part of total water used, the rate and volume of water used during a fire can be so great that it becomes the deciding factor in engineering the capacities of water storage, water supply and water distribution.

The EPA requires water distribution mains serving fire hydrants be designed to a minimum size of 6-inch diameter. Further, the regulations require that system pressures to exceed 20 psi at ground level for all flow conditions including fire flow conveyance. Generally, a water system is designed to provide fire flows somewhere between the minimum of 500 gpm to 2,000 gpm in communities the size of Whereville. Generally, a fire flow that requires a large amount of water storage that cannot be readily "turned over" through water use could result in a problem with stagnant water and, therefore, domestic water use should be considered when selecting the desired fire flow.

The fire flow recommendations by the ISO for residential districts, varies based on the type of structure as well as structure separation. In small communities such as Whereville, it is recommended that fire flow requirements be considered as 500 gpm for the residential areas with more than 10 feet of separation and a minimum of 1000 gpm for the school, commercial areas and the churches within the community. The maximum flow considered for the Village would be 1500 gpm. The recommended fire flow periods would be 2 hours minimum and 4 hours maximum.

The review of the water system distribution using a hydraulic model shows that the flow capability can only meet the minimum requirements of 500 gpm at the water tower. It is also assumed that the deficiency is attributed to inadequate water main sizing to convey fire flow and inadequate tower height to provide adequate pressure on the system to convey fire flows.

Current and Projected Water Storage

Basis of Analysis - Existing Storage

Finished water storage and system pressures are maintained by the existing 50,000 gallon tower. The tower was constructed in 1950. The tower height to overflow is 98 feet above grade (42.5 psi). The tower is located in the northern 1/3 and western 1/3 of the community. The tower is maintained on a regular basis by a tower specialty firm. The tower has exterior lead paint which is contained by paint overcoat systems. The interior of the tower is reported to be pitted and is epoxy coated. The tower is judged to be in fair to poor condition and nearing the end of its useful life. The tower height is judged deficient to maintain adequate pressure under all conditions of use in the distribution system.

Analysis - Future Water Storage Needs

Distribution system storage serves several purposes. In all cases, water that is stored needs to be readily available to the distribution system upon demand. The various components of storage volumes are explained as follows:

Emergency Storage: Water to be used in case of a power outage when no standby power is available or in case of an accidental equipment breakdown. For the purposes of this report, an equipment breakdown of 4 hours is assumed using the average daily usage as the base demand.

Reserve Storage (or Equalizing Storage) Water needed to equalize supply and demand during days when high peak hourly flows are required. It can also be used to equalize supply and demand over longer periods of high consumption. Equalizing storage volumes to meet peak demands normally range from 5 % to 40% of the average day use in small to moderate communities. This study has utilized 25% of average daily use for reserve storage volume.

Fire Flow Storage: Water is also needed for fire-fighting purposes. This volume is generally equal to the recommended fire flow needs of a community times the estimated duration of the fire. The recommended fire flow demands were previously stated to range between 500 and 1,500 gpm for a duration of 2 hours to 4 hours. For the purpose of fire flow storage calculations, 1,000 gpm for 2 hours will be used.

The sum of these three volumes added together approximates the storage needs for the community. As a check, many engineers use a "rule-of-thumb" of one day's consumption plus fire flow storage for elevated storage needs.

Based upon the above criteria and the design average daily usage of 25,000 gpd, the storage needs for the community are:

| Average Dav Use | 25,000 gallons |
| --- | --- |
| Emergency Storage | 4,167 gallons |
| Reserve Storage | 6.250 gallons |
| Subtotal for Svstem Use | 35,417 gallons |
| Fire Flow Storage | 120,000 gallons |
| Total Storage Needed | 155,417 gallons |
| Total Existing Storage (available) | 50 000 gallons |
| Storage Volume Shortage | 105,417 gallons |

The above considerations for storage can be offset by capacity of wells and treatment systems to supply water during times of fire demand. The current well capacity of 120 gpm would provide 14,400 gallons during a 2 hour fire demand period. The resultant shortfall would be 91,000 gallons. The provision of this amount of excess storage for fire flow considerations would create water quality issues due to the lack of turnover in the tower. Therefore, it is recommended that storage considerations be based on flow requirements exclusive of fire flows. The recommended minimum storage requirements for the community would then be 35,000 gallons. While this volume does not meet fire flow requirements, it does represent a reasonable compromise to maintain acceptable water quality for a small water system. In elevated tower sizing, 50,000 gallons would be the recommended size tower for the community since this volume is considered the minimum size to construct for elevated storage.

Water Storage Options - Results of Analysis

Elevated Water Tower

The existing water tower is found to be deficient due to the height necessary to maintain adequate pressure in the distribution system. The existing tower is near the end of a normal 60-year useful life. A new tower, proposed as a replacement, should provide a minimum pressure on the system greater than the maximum pressure currently available. It is recommended that the system pressure be increased to 58.5 psi, which is 135 feet to the overflow. The tower size recommended would be 50,000, the existing tower capacity. The recommended tower size of 50,000 exceeds the projected system storage needs, however, the 50,000 gallons is considered a minimum size requirement for elevated storage.

Combination Ground Water Storage and Hydropneumatic Tank

An alternative mechanism in the smaller community to provide water storage would be a combination system of ground storage with booster pumps and a pressure tank. This system would meet the recommended storage needs and provide the necessary redundancy and emergency operations necessary for this system. The Administrative Code Rules and Regulations establishes component sizing and to meet the rates of use for the Village. The major components and their recommended sizing are:

| Ground Storage Tank - 3 @ 12,500 gallons | 37,500 gallons |
| --- | --- |
| Pressure Tank | 10,500 gallons |
| Booster Pump - 2 Required | 175 <gpm each |
| Building to House Equipment & Tanks | 1,080 sf |
| Standbv Generator | 60kw |

The use of multiple smaller tanks for the ground storage would assist system maintenance of the ground storage system and eliminate painting of steel tanks.

Current and Projected Water Supply and Treatment Needs

The Whereville water supply is drawn from the Maholer Aquifer. The aquifer at this location is a sand and gravel deposit approximately 130 feet in thickness. The existing Well No. 2 was constructed in 1990 to a depth of 134 feet. It has 17 feet of 6-inch diameter x 12 slot screen. The casing is black steel. This well replaced the original water supply well, Well No. 1, which was abandoned when well No. 2 was constructed. The aquifer is artesian in this location. The static level is approximately 12 feet below grade and the pumping level at 120 gpm is approximately 19 feet. The Well Pump has a 10 hp Goulds Submersible with a 3-inch galvanized column pipe. The well pump is set at 84 feet.

Whereville analyzes samples on a regular basis for compliance with the maximum contaminant limits per the EPA and USEPA drinking water standards. The supply is in compliance with applicable rules.  The supply is treated with phosphate addition to sequester iron and manganese. The sequestering process coats the iron and manganese ions to limit their oxidation and formation of precipitants that will stain. Heating of the water will have some tendency to break the physical bond and hence some staining of laundry, sinks and bath fixtures can occur. The sequestering agent appears successful. The remaining treatment provided the water is fluoride addition to maintain sufficient fluoride in the system and chlorine addition to provide disinfection. The current chemical feed equipment is in good condition.

Needs Analysis - Water Supply, Water Quality and Treatment

Water Supply Needs

A review of the condition of the existing well indicated the existing water supply for Whereville requires remedial measures. A problem with the well pump column pipe was investigated in December, 2023. The existing Well Screen was found to be approximately 80% plugged with growth or calcification. The existing well pump and column pipe were considered to be in poor condition and in need of replacement. It is recommended that the remedial measures for cleaning the well screen and providing a new replacement of the pump and column pipe be implemented as soon as possible.  The existing well does not have an alternate source of power. It is recommended that a manual transfer switch and a generator suitable to start and operate the 10 hp well pump and the chemical feed pumps be provided.

Water Quality Treatment Needs

The supply is in compliance with applicable rules. The maximum contaminant limit for iron exceeds the Maximum Contaminant Limit required by the regulations, however, communities with less than 300 connections are not required to comply with the limit. The supply is treated with chemicals to sequester iron and manganese.

The majority of the Village Board indicates they use the water supply for drinking purposes. Some members do provide filters or other devices to condition the water supply for drinking purposes. The water does not have an objectionable taste. One individual could detect a metallic taste. No odors were noted present in the finished water. The staining of fixtures and clothing during washing were the principal issues cited concerning water quality. Most of the staining was noted as red, though one noted black and a second noted yellow as the offending color. The staining issue is principally due to the 1.5 mg/1 iron levels in the supply. Iron. A secondary recommended standard for iron is 0.3 mg/I. Levels in excess of this value will likely cause staining. In addition, manganese greater than 0.07 mg/I or a combination of iron and manganese in excess of 0.16 mg/I will cause staining. The manganese levels are less than .067 mg/I for this supply.

Sequestering encapsulates the iron and prevents oxidation and precipitation. Heating of the water will have some tendency to break the physical bond and hence some staining of laundry, sinks and bath fixtures can occur. The sequestering agent appears successful. Filtering devices installed after hot water heaters may assist prevention of staining of laundry and sinks. On the basis that the supply does meet standards and the opinions stated by Village Board members, no additional treatment process needs will be considered by this report.

On the basis that the water quality is achieved with the current systems, no additional treatment is recommended.

Water Quality Source Protection

The EPA Consumer Confidence Report notes that the existing Village well is considered at risk to pollution due to a well located approximately 30 feet south of the existing Village Well No. 2. This well was constructed by the railroad to provide water to the steam locomotives. The well has been orphaned from ownership by the railroad and it appears the property it is located on has been vacated. It also appears the property is now designated Right of Way of the Village.

A search of construction records of the Well has proved unsuccessful. It appears that the construction of the well is a drilled well to the Maholer Aquifer and finished at least 110 feet below ground. The well casing, diameter unknown, was terminated below ground and a concrete collection reservoir was constructed. The collection reservoir is an octagonal reinforced concrete structure with a bottom slab and top slab. The structure has a 26 foot outside dimension. The apparent wall thickness is 12 inch and roof thickness is 8 inches minimum. The depth of the structure is 28 feet. The water level in the reservoir is 9 feet below ground surface. It is estimated that the structure is holding approximately 70,000 gallons of water.

The collection reservoir has not been successfully dewatered due to the artesian characteristics of the aquifer and the apparent capacity of the drilled well. The reservoir was pumped at rates exceeding 500 gpm for more than 14 hours and the reservoir drawdown was less than 6 inches during a major fire in the community. The well is fitted with a 4 inch suction pipe through the collection reservoir roof.

We have reviewed the regulatory criteria for collection reservoirs as a structure which requires protection. It was found that the access opening and the penetration of the top of the reservoir do not provide the minimum vertical clearance of 2 feet above existing ground. We do not recommend correction of this deficiency due to other structural considerations for the reservoir. We recommend the collection reservoir be abandoned since its water tightness and retention ability are suspect in a structure that is at the end of a normal 50 year design life.

The EPA has recommended the well be abandoned in accordance with the applicable codes for abandoning wells. The abandonment of the collection reservoir would require action to modify the well or abandonment of the well. Well modifications which would be necessary to abandon the collection reservoir and retain the well would be accomplished by raising the casing, encasement of the well casing with concrete from the bottom of the collection reservoir to near the surface and installation of a pitless adapter and other well finishing details. The finishing of the well in this fashion would leave the well usable as a source of fire water for the fire department or as a potential second well for the Village. The abandonment of the well would require grouting the well to provide a seal.	It is recommended that the well be retained and that the collection reservoir be abandoned.

Current Water Distribution System and Recommended Improvements

After a water supply is obtained and treated, the distribution system must deliver the water to the ultimate users or to storage. To be adequate, a distribution system must be capable of furnishing an ample supply of water, with satisfactory quality, to all customers throughout the water system. The distribution system may include booster pump(s), pipelines, control valves, hydrants, service connections, valves and meters. The system must maintain adequate pressures for normal use, and when necessary, high flows required for fire protection. The above section on the water tower recommended that the water storage would not include consideration of fire flows.

The pipes of a distribution system are sized utilizing hydraulic criteria such as the length of pipe, friction loss, elevation, restrictions, rates of flow, and location. The most important criteria is configuration, the pipes should be arranged in a gridiron or looped pattern. This gridiron pattern allows water to reach a location in the system through more than one path. A grid system also allows maintenance and repair of sections of the distribution piping without totally cutting off the water supply to large areas; thus, a water main break can be isolated and repaired while service is supplied by another leg of the gridiron system. In actual practice, however, there are

economical and logical reasons to have some "dead end" pipes in the system. The "dead end" pipes are usually located where water service is required for only a few users or where a future extension is contemplated for completion of the grid.

The following recommendations for the water distribution system size and configuration would meet or exceed applicable EPA Regulations:

- Deliver water under normal flow conditions at pressures ranging from 35 to I 00 psi.

- Deliver flushing flows (minimum 2.5 fps velocity with double feed) at a minimum pressure of 20 psi.

- Water mains shall be 4-inch diameter minimum for incorporated areas.

- Valves to be a maximum of 800 feet apart.

- Hydrants should be sized for flushing and located approximately 600 feet apart and at all dead ends.

Good engineering practices also come into effect when planning and constructing distribution piping. The velocity in the water mains should not exceed five (5) feet per second under design conditions and consideration should also be given to the amount of friction loss in the pipes to minimize operation costs for the pumps and motors.

Valves should be adequately located and maintained throughout the distribution system to enable a section or sections of the piping to be shut off for maintenance, repair, or construction of an extension to the system with minimal service interruptions to users. Hydrants should be strategically located to assure a reliable flow of water for flushing purposes.

Distribution System Analysis

The existing water distribution system was built in 1950. Minor improvements and changes have occurred since the original construction. The existing pipes are reported to have deposition in the mains reducing their effective diameter. The system has several dead ends which lead to water quality issues and prove difficult to flush. The system has experienced several water main breaks which have been attributed principally to the age of the system.

The system was modeled using the peak day water use and the system ability to supply flow in excess of the peak rate of flow. The model demonstrates the system is capable of flow in excess of the peak system demands exclusive of fire flow. The model which is presented in picture form indicates the majority of the excess flow is available in the one square block area centered on Palmer and extending from Melvin to the tower located on John St. Areas of the community east of the railroad have limited flow conveyance of less than 200 gpm. Areas principally south of South Street have flow capacity of 100 gpm or less. This has proven to be inadequate based on user reports of limited water flow ability for multiple and simultaneous use in the homes.

Project Cost Estimates

Project costs include administrative, legal, engineering, property acquisition, utility service extensions and other items as appropriate to implement a project. The project costs outlined below use customary estimates for administrative and legal at 4% of the improvement cost. The engineering cost has components for engineering design and permitting and engineering assistance for construction guidance, on site observation, assistance during startup and other items which are project specific. The costs for the services use an estimate of engineering design and permitting at 10%. The bid assistance and construction guidance is estimated at 5%. The construction observation is budgeted at 6% and the administrative assistance for grants and loans are 2%. The actual costs for the services may vary depending on the time periods of services and other factors not specifically known at this point.

Project cost budgets should also include escalation factors for probable construction costs at the time when a project is bid. The outlined projects are escalated to a bid date of October 2026, which is 24 months from the current time to allow project funding timelines necessary to secure grants for the projects. The inflationary factor of 4 % per year is suggested as a reasonable value for the current economic conditions. The inflationary value for the two-year period is 8.16% which has been rounded to 8%.

Water System Needs Prioritization

The water system improvements are prioritized based on critical needs. The projects are listed from highest to lowest priority.

The Well No. 2 improvements, which includes cleaning the screen, installation of a new pump and column pipe is rated the highest priority since no the water supply currently does not have any backup or redundant features. The primary purpose of the project is public health in provision of water to the system without interruption. This project includes installation of a standby power generator to drive the current well and the chemical feed systems. The estimated construction cost is $27,000.

The next priority project is the completion of water main improvements for the distribution system. The system has limited capacity to deliver water to meet peak demand and maintain adequate system pressure. This places the users at risk of contamination of the system. The project includes installation of approximately 3300 If of new water main, valves and hydrants. The system improvements serve existing users of the system and replace seriously undersized water mains currently serving the homes. The estimated construction cost is $155,000.

The third priority project addresses the issue of source protection. The Village currently has access to a well which was initially constructed on Railroad Right of Way. It appears that the right of way was abandoned in favor of the Village and is currently a Village right of way.

The modification of this well by abandoning its collection reservoir and finishing the well in accordance with standards would provide a second water source for the Village. The pitless unit could be connected to a hydrant which could serve the need for connection of a fire truck for their firewater needs. The estimated construction cost for this project is $39,000.

The next priority is replacement of the water tower. This project would raise distribution pressures by increasing the distribution pressures. The discussion section provides the option to eliminate the water tower by switching the system to a hydropneumatic tank for maintaining system pressure. This option eliminates the cost of painting and repairs for the elevated structure. The timeframe for completion of this project is in the next 5 to 10 years. The construction cost is estimated to be $ 402,000.

The total needs for the system have been estimated and prioritized. The estimated construction cost of the four improvements totals to $623,000. It is recommended that the needs be addressed with 2 separate projects.

CONCLUSIONS

Water System Conformance to Standards

The water system was reviewed on the basis of conformance with applicable standards. The system was found to meet applicable standards for the existing well and treatment systems. The system was found deficient and would not meet applicable standards for source protection and distribution system size and pressures. The system does not have redundancies for the water supply since it only has one operational well. The system does not have the ability to provide emergency power during prolonged loss of electrical power. The distribution and storage system were not sized to provide fire flows to the community.

Proposed Improvements

Water Storage

The water storage volume provided is adequate for the community. The tower is at the end of its useful life and is not of sufficient height to provide adequate pressure in the distribution system under peak flow conditions. It is recommended the tower be replaced with a combination of ground storage, hydropneumatic tank, booster pumps and a standby generator. It is recommended that the distribution system operating pressure be increased to 58.5 psi. The water storage requirements were concluded to be 35,000 gallons/day.

Water Supply and Source Protection

The condition of the existing well screen and the well pump and column pipe were found to be in poor condition. The report recommends the screen be cleaned and a new well pump and column pipe be provided. The system does not have any emergency power. A standby generator and manual transfer switch were recommended. The presence of the railroad well presents a risk of contamination of the water supply. It is recommended that this well be finished to the surface and that the collection reservoir be abandoned. The report concluded the existing well has adequate capacity.

Water Distribution

The water distribution and elevated storage were built in 1950. The system has existing 2-inch lines in the distribution system. The system has limited looping of water mains in the areas with the undersized mains. The report recommends improvements to the water distribution system to replace the majority of the undersized water mains and provide system looping as appropriate.

The report concludes the distribution system should not be sized for fire flows.

Water Distribution Map

Photos

Whereville

Water Plant, Wells, Elevated Tank

Well #2

Well #3

Treatment Plant

Pump House

Elevated Tank